The invention relates to the water softening technology and may be used in power engineering for softening of processing water. The method for softening  water includes mechanical cleaning of water by passing it through a mechanical filter, further passing of water through a sulfo-carbon filler in a cationic filter, and periodical restorating cycles of filtering function of sulfo-carbon filler by loosing, regenerating and washing. Due to the improving of working parameters of sulfo-carbon filler in the cationic filter before guiding the water into the filter, the water is exposured to a permanent magnetic field by transmiting it with speed of 3-3,5 m/s perpendicularly to magnetic flow lines with intensity of 1,3-1,4 kGs/cm2. The water is softened in the cationic filter over the range of total hardness of from 1-0,9 mg ekv/l to 0,25-0,2 mg ekv/l. Due to the fact that water is softened by using this method and by holding the determined technical characteristics, produktivity and resources of the sulfo-carbon filler are increased. An improvement of these parameters of the cationic filter is achieved by using an influence of the magnetic field.